UNIVERSITY HOSPITAL EXPANSION

AN 05163

ECCLES CRITICAL CARE PAVILION

(BLDG 529) VERTICAL EXPANSION
SALT LAKE CITY, UTAH

Project or Building Name 

227500-

DCFM Number

High Pressure Steam Domestic Water Heat Exchanger 

University/Institution Project Number 

 


 SEQ CHAPTER \h \r 1SECTION 227500
HIGH PRESSURE STEAM DOMESTIC WATER HEAT EXCHANGER
PART 1 - GENERAL

1.1 RELATED STANDARDS/DOCUMENTS

A. All applicable sections of the Mechanical Requirements are part of the work of this Section.

a. Division 23 Section “Mechanical Vibration and Seismic Controls for HVAC”

b. Division 23 Section “HVAC Insulation”

c. Division 23 Section “Meters and Gages for HVAC”

d. Division 23 Section “Hydronic Piping and Valves”

e. Division 23 Section “High Pressure Steam Piping”

f. Division 23 Section “Instrumentation and Controls” 
g. Division 22 Section “General Plumbing Requirements”

h. Division 22 Section “Operation and Maintenance of Plumbing”
i. Division 22 Section “Electrical Requirements for Plumbing Equipment”
j. Division 22 Section “Thermometers and Gauges” 
k. Division 22 Section “General Duty Valves for Plumbing Piping
l. Division 22 Section “Plumbing Insulation”
B. The American Society of Mechanical Engineers (ASME), Boiler and Pressure Vessel Code, Section VIII, Division 1 – Rules for Construction of Pressure Vessels.
C. The National Board Inspection Code (NBIC).
D. American National Standards Institute (ASME).
E. American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE).
F. Standards of the Tubular Exchangers Manufacturers Association (TEMA).

G. International Building Code (IBC).
H. Local health and safety codes.
I. Current industry standards.
1.2 SUMMARY

A. This section includes TEMA class “C” high pressure steam (HPS) to steam, domestic water heat exchanger for use with high pressure steam; also known as instantaneous water heater.
B. Instantaneous water heater to be vertically mounted with a space to remove the tube bundle without disturbing the shellside connections.
C. The instantaneous water heater shall be furnished as a complete package ready for installation. All components for the instantaneous water heater shall be factory mounted, piped, and tested and the unit shall be shipped from the factory as a complete unit ready for installation.
1.3 DEFINITIONS

A. High Pressure Steam (HPS) – operates at pressure of 15 PSIG or more.
B. Channel – component of the instantaneous water heater with high pressure steam inside the tubes. 

C. Shell – component if the instantaneous water heater with water outside of the tubes. 

D. Tube Bundle – heat transfer barrier between the high pressure steam and domestic water. 

1.4 SUBMITTALS

A. Submit product data in accordance with applicable submittal standards. Submit the following:

a. Instantaneous water heater top assembly drawing – detailed equipment assemblies, dimensions, weights, required clearances and the location and size of each field connection
b. Operation and maintenance manual

c. Control component part list

i. Temperature Control
ii. Safety Control
iii. Any additional instrumentation
d. Instantaneous water heater performance specifications

e. Instantaneous water heater material thickness verifications for the specified operating pressure for the following
i. Shell

ii. Channel

iii. Tubesheet

iv. Tubes
f. Instantaneous water heater seismic loading calculations

1.5 QUALITY ASSURANCE

A. Product Options: drawings shall indicate size, profiles, performance, and dimensional requirements of the instantaneous water heater and are based on the specific equipment indicated.
B. ASME code “U” or “UM” stamp compliance: design, manufacture, test and mark instantaneous water heater to comply with ASME Boiler and Pressure Vessel Code, Section VIII, Division 1 – Rules for Construction of Pressure Vessels. Each instantaneous water heater must be registered with the National Board of Pressure Vessel Inspectors.
C. Each instantaneous water heater shall be factory tested prior to shipment. The factory hydrostatic test pressure shall be 1.3 times the design pressure or as required by the end user/owner. This test shall be provided for each individual tube and shell side of the instantaneous water heater. Provide ASME Code and National Board of Pressure Vessel Inspectors inspection and stamping for both the tube side and the shell side; the manufacturer must furnish shop inspection certificates. Individually certified shell and tube sections are not acceptable. 

D. Design all appurtenances with allowance for expansion and contraction of all parts. Arrange the pipe and fittings to prevent rubbing and abrasion as the system parts move during temperature changes. 

E. Each instantaneous water heater shall have factory installed (welded) saddles with drilled holes for anchors. One end must be slotted to allow for expansion and contraction. 

F. Prior to shipping, the instantaneous water heater internals shall be thoroughly cleaned. All exterior surfaces shall have a coating suitable for the expected operating temperature specified. The coating shall include the saddles. Coating applications must be in accordance with coating manufactures recommendations. 

a. Carboline Thermaline 450
b. Thurmalox 225HD
G. General Construction: Provide for convenient removal and replacement of the tube bundle through flanged shell and channel openings. The tube bundle weight shall be indicated through stamping or nameplate identification on the tubesheet. All connections shall be tight and free of leaks at test and operating pressures. Provide a minimum of 0.0625" corrosion allowance for all carbon steel pressure parts. 

PART 2 - PRODUCTS

2.1 MANUFACTURERS

A. Manufacturers: Subject to compliance with requirements, provide by one of the following:

a. Howard’s Engineering Heat Transfer Products – Pico Rivera, CA.

b. Substitutions must meet the following minimum requirements

i. Ten years of experience manufacturing shell and tube instantaneous water heater for use in HPS systems

ii. Demonstrate the engineering and manufacturing knowledge to manufacturer shell and tube instantaneous water heater for use in HPS systems 

iii. Familiarity with the TEMA standards

2.2 HIGH PRESSURE STEAM INSTANTANEOUS WATER HEATER
A. The instantaneous water heater shall be installed where shown on the drawings and schedules and constructed as noted in the specifications.
B. TEMA “C” class heat exchanger, type BEU configuration. 
C. Design
a. Performance – as specified

b. HPS clean factor – at least 0.0005 HR-FT²-°F/BTU, or as specified

c. Domestic clean factor – at least 0.0005 HR-FT²-°F/BTU, or as specified
D. Channel 

a. Service – HPS
b. Made from pressure vessel quality carbon steel. Castings are not acceptable.

c. Rated for at least 150 psi at 450(F and a minimum of 150 psi at 0(F.

d. ASME B16.5, 150# (minimum) flanges for connections 2” and larger.

e. ASME B16.11, 3000# (minimum) socket weld couplings for HPS vent (at the highest point) and drain (at the lowest point). ASME B16.5, 300# flanged connections are acceptable.

f. ASME B16.11, 3000# (minimum) NPT threaded coupling for HPS instrumentation connection points. ASME B16.5, 300# flanged connections are acceptable.
g. Gaskets must be engineering per the manufacturer’s recommendation, taking into account pressure, temperature ratings and relative gasket surface. Fiber sheet gaskets are not acceptable. 

h. Provide lifting lugs for all channels exceeding 200 pounds.

E. Shell 

a. Service – domestic water.
b. Made from type 316/L stainless steel. 
c.  Rated for at least 150 psi at 350(F and a minimum of 150 psi at 0(F.
d. Minimum shell thickness schedule 10S per ASME B16.19.

e. ASME B16.5, 150# (minimum) flanged for domestic water inlet and outlet
f. The overall length to diameter ratio of the instantaneous water heater shall not exceed 5:1.  
g. Gaskets must be engineering per the manufacturer’s recommendation, taking into account pressure, temperature ratings and relative gasket surface. Fiber sheet gaskets are not acceptable. 

h. Provide lifting lugs for all shells exceeding 200 pounds.

i. Vertical support stand designed to withstand bending during service.
F. Tube Bundle

a. Service – heat transfer barrier between the high pressure steam and domestic water. 
b. Single wall construction.
c. Removable type “U” tube. 

d. Designed to freely expand and contract as determined by the service. 

e. Designed for at least 150 psi at 350(F and a minimum of 150 psi at 0(F on the channel side; at least 150 psi at 350(F and a minimum of 150 psi at 0(F on the shell side. 

f. Tube holes must be finished in a manner that will not create a direct leak path from one side to the other. 
g. Tubesheet 
i. Must be made of type 316/L stainless steel.
ii. Must have a full bolt circle with at least (4) shoulder bolts spaced evenly to retain the shellside gasket while servicing the channel. Tapping’s for the shoulder bolts are not acceptable.
iii. Must have at least (2) pull bolts spaced at least 180( apart to aid in removal of the bundle, on the channel side of the tubesheet. The diameter of the pull bolts must be at least 0.50”. 
h. Tubes

i. Must be made of single wall copper tubing. Substitutions should be submitted to the owner for final approval. Stainless steel is not acceptable for use in HPS systems – no exceptions. 
ii. Diameter to be either 0.500”, 0.625” or 0.750”. 
iii. The tube pitch must be arranged to allow for ease of cleaning. 
i. Supports

i. Must be made of virgin grade Teflon sheet.
ii.  Tube hole clearance to be as specified by TEMA, no exceptions.
iii. Baffle supports to be as specified by TEMA. 
iv. Adequately spaced to eliminate the possibility of tube vibration while complying with all other performance specifications. 
v. Shall be fabricated and arranged to prevent abrasion and wear on the tubes during service. The design shall allow convenient removal and replacement of the tube bundle from shell. 
G. Controls

a. All controls to be mounted in a NEMA 4X (minimum control panel)
b. HPS control system

i. HPS Control Valve

1. ASME B16.5, 150# (minimum) flanges for the inlet and outlet

2. 2-way flow pattern

3. Pressure drop through the control valve as specified
ii. Electronic or pneumatic

iii. True fail safe

iv. HPS flow eliminated during a high temperature scenario or power failure

c. Domestic hot water temperature control system

i. Reverse acting
ii. Control system actively monitoring the temperature of the domestic hot water and modulating the HPS control valve – flow – accordingly
d. Domestic hot water over temperature control system

i. Must be independent of the temperature control system

ii. Eliminates the flow of HPS (closes the valve) in the event that the domestic hot water temperature exceeds the set point. 

e. Pressure relief valve
i. Adequately sized to accommodate the performance of the domestic hot water heat exchanger

ii. Set pressure – 150 psi
iii. ASME Code Section VIII liquid pressure relief valve sized to relief the total output (in GPM) of the domestic hot water heat exchanger.
f. HPS Pressure gauge

g. Domestic hot water thermometers, 50-250°F range
H. Insulation

a. The shell insulation should not be less than 1.50” thick with a 0.016” thick stainless steel moisture barrier jacket
b. The channel shall be insulated with 2” thick removable blanket insulation, fastened by wire
PART 3 - EXECUTION

2.1 HIGH PRESSURE STEAM INSTANTANEOUS WATER HEATER
A. Verify that instantaneous water heater is installed and connected according to the Contract Documents.
B. Adjust flows and controls to deliver specified performance.
C. Test and adjust controls and safety devices. Replace damaged and malfunctioning controls and equipment.

2.2 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner’s maintenance personnel to adjust, operate, and maintain instantaneous water heater as specified below:
a. Train Owner’s maintenance personnel to procedures and schedules for starting and stopping, troubleshooting, servicing, and maintaining instantaneous water heater.

b. Review data in maintenance manuals.  Refer to Division 1 Section “Contract Closeout.

c. Review data in maintenance manuals.  Refer to Division 1 Section “Operation and Maintenance Data.”

d. Schedule training with Owner, through Architect, with at least seven days advance notice.

END OF SECTION 227500
Month/Day/Year

Consulting Engineers
Documentation Phase


